Load Testing Circuits in Buildings

Kenyon. A. Riches

http://www.kennedyelectric.com/SureTest/Suretest-LoadtestingCircuitsinBuildings.htm

Inspection of new construction electrical systems by municipal building inspectors is normally visual only - at least during construction. After completion of the electrical installation, instrument testing of branch circuits, if done at all, is usually done with a simple multi-meter, polarity checker and GFCI checker. When inspection of building wiring is required of existing structures, the inspection often is also visual only. The age and type of wiring are noted, along with the type of overcurrent protection (circuit breakers/fusing) and the general condition of the main and sub-panels. Code violations and “unprofessional” workmanship are noted for correction. If there are suspected deficiencies in the wiring as a result of this inspection, testing of a circuit with a multi-meter, might be done, however, static testing will not identify defects such as poor or loose connections, or damaged conductors. When current flows through these high resistance defects, heat buildup results at the connections.

The NFPA reports [1] that during the period 1989-1993, an average annual total of more than 162,400 fires/year occurred in non-residential structures, resulting in $2.9 Billion of property damage and 205 deaths. 16,600 or 10.2% of these fires were caused annually by Electrical Distribution Systems.

The NFPA also reports [2] that from 1988-1992, there was an average annual total of 446,300 fires in homes, resulting in 3,860 Deaths and $4.4 Billion property damage. 42,300 (9%) of these fires were caused each year by Electrical Distribution Systems. The largest portion of fires caused by electrical distribution systems (48%) were caused by faulty fixed wiring, receptacles and switches.

Electrical Distribution Equipment Fires in U.S. Homes2

1988-1992 Average

| Cause of Fire | No. Of Fires |
| --- | --- |
| Total Electrical Distribution System | 42,300 |
| Fixed Wiring | 15,400 |
| Switches, Receptacles, Outlets | 4,800 |

An article by Smith & McCoskrie [3] summarized the results of an in-depth investigation of 149 residential fires caused by the electrical distribution systems. Of the fires occurring as a result of:

- faulty fixed wiring - poor or loose splices, damaged connectors, improper installation and ground faults accounted for 94% of these fires.

- receptacles and switches - loose or poor connections accounted for 59% of these fires.

- Lighting fixtures - loose or poor connections accounted for 37% of these fires.

Most of these faulty circuits and receptacles could have been previously identified as hazards with a 15-ampere load test, and the very real probability exists that several thousands of these fires could have been easily prevented!

Most fixed wiring and receptacle hazards are hidden from inspection and cannot be identified with static non-load tests. However, easy-to-use, safe and cost-effective plug-in testers are now available that test the circuit under a 15-ampere load. This test can identify certain types of deficiencies in branch circuits, specifically loose connections and damaged conductors.

The testers determine the resistance of the circuit - including the wire and all splices and connections - under a 15 ampere load. A microprocessor measures the voltage under no load and under a 15 ampere load and calculates and reads out the % Voltage drop on the circuit. Excess voltage drop indicates damaged conductors, poor connections/splices, overlong circuits, and/or undersized wires. Not only can the reduced voltage cause damage to or malfunction of equipment (which may cause a fire), but the resistance in the fixed wiring which causes excess voltage drop generates heat - which can be a definite fire hazard - especially if the cause of the excess voltage drop is a point source such as a loose connection.

How much voltage drop is excessive? The NEC (FPN No. 4) states” Conductors for branch circuits as defined in Article 100, sized to prevent a voltage drop exceeding 3 percent at the farthest outlet of power, heating and lighting loads or combinations of such loads and where the maximum total voltage drop on both feeders and branch circuits to the farthest outlet does not exceed 5 percent, will provide reasonable efficiency of operations.” The IEEE recommends that the resistance of any conductor in a branch circuit should not exceed 0.25 ohms. A complete circuit of 2 conductors - or maximum total of 0.5 ohms - would yield a voltage drop of 6.2% under a 15 ampere load on a 120 volt circuit.

For example, assume a circuit has a total voltage drop of 8.3% when measured under a 15 ampere load. Assume further that the circuit's normal wire and connector resistances yield a voltage drop of 5% (the NEC maximum level for reasonable efficiency), and that any voltage drop in excess of that amount is attributed to a point source of resistance (connection, splice, etc.). The additional voltage drop of 3.3%, or 4 volts in a 120 volt circuit, means that the loose or damaged connection has a resistance of 0.27 ohms, which - at 15 ampere current flow - would generate a point source of heat of 60 watts. A 60-watt point source of heat in prolonged contact with combustible material can cause ignition.

The Philadelphia Housing Development Corporation requires contractors to perform the 15-ampere-load test prior to insulating existing homes with insulation blown into attic crawl spaces in older row homes. [4]

Prior to instituting the test, smoldering fires were associated with half a dozen installations. The PHDC found that 70% of the homes flunked the 5% threshold on the voltage drop test with “a cluster around 6%”. The PHDC arbitrarily established 10% as an unacceptable voltage drop, beyond which the contractor must replace the circuit prior to proceeding with the insulation project. PHDC has been using this criteria successfully for 2 years (no fires in 2,500 installations).

Testing wiring circuits under full load is also recommended by the Occupational Safety & Health Administration - who teaches the use of this test in OSHA safety classes at the OSHA Technical Institute in Des Plains, IL.

After using the Voltage-drop-under-15-ampere-load test for eight months, Steve Scully of the National Assoc. of Home Builders Research Center stated “Because the tester is able to quickly and safely apply a full load test to the circuit, we can test all circuits in a house for hidden, sometimes deadly flaws within minutes”. Simple-to-use, the tester isolates hazards using simple logic as the inspector moves along the branch circuit.

Based on the ease of application of this test, the Consumer Product Safety Commission recommended to the NFPA 73 technical committee - the inclusion of the 15 ampere load test in NFPA 73, the inspection procedure for one and two-family dwellings.

Chuck Barenchi, Insurance loss control inspector for Farmers Insurance in California, says, “By testing circuits under full-load, I feel a lot more comfortable signing off on the acceptability of a building's wiring system.”

The increased use of non-linear loads resulting from increased use of switch-mode power supplies increases the loads to be carried by branch circuits. With this trend and the fact that wiring deteriorates due to aging, the likelihood increases that fires will be initiated by faults in fixed wiring and receptacles, hence the increased need for a full load test.

Static tests will also not identify undersized wire. Often the inspector will approximate the length of the wire run, and calculate the required wire size. By testing the branch under load at its last receptacle, the resistance of the entire circuit is determined and can easily confirm whether the wire is sized correctly.

The measurement of ground impedance under load will also identify loose connections or other causes of inadequate grounding, which are not only hazards because of inadequate fault current paths, but they often render useless the protection of computers and other expensive equipment by devices that rely on a good quality ground.

The dynamic testing of branch circuits under full load has been proven to be effective at identifying hazards and is fast becoming the preferred method. The identification of deficiencies in branch wiring and receptacle and the isolation of hazards such as inadequate grounding, loose connections, Improper wiring can prevent thousands of fires if used routinely by inspection personnel.

The author is president of Industrial Commercial Electronics, manufacturer of SureTest circuit analyzers at 590 Young Street, Buffalo, NY 14225. (800) 442-3462; (716) 692-3061.fax

ADVERTISEMENT:

The SureTest patented circuit analyzer takes only seconds to test each outlet and circuit under a full load. It reads out the line voltageunder no load, the % voltage drop under both a 15 and a 20 ampere load, the ground impedance in ohms, common mode voltage (voltage between ground and neutral), and estimates the total ampere load on the circuit (calculated from common mode voltage). This instrument also detects incorrect wiring, false grounds (the illegal connection of ground-to-neutral at the outlet), and measures the exact trip point of a GFCI (in ma) - independent of line voltage variations.

#### Footnotes

[1] Miller, Alison NFPA U.S. Home Product Report 1988-1992 (Appliances & Equipment) Aug. 1994

[2]NFPA U.S. Home Product Report 1988-1992 (Appliances & Equipment) Alison L. Miller August, 1994

[3] Smith, Linda & Dennis McCoskrie, “What Causes Wiring Fires in Residences” Fire Journal Jan/Feb 1990: 19-24, 69

[4] Kinney, Larry “Assessing the Integrity of Electrical Wiring” Home Energy Sept/Oct 1995: 5,6